## EDE
# Proposal_Engineering-Data-Exchange - B.I.G.-EU
PROJECT_NAME | CC BACnet
VERSION_OF_REFERENCEFILE | 31000
TIMESTAMP_OF_LAST_CHANGE | 2012-10-22
AUTHOR_OF_LAST_CHANGE | M. Schildt
VERSION_OF_LAYOUT | 2.1
#mandatory | mandatory | mandatory | mandatory | mandatory | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional
# keyname | device obj.-instance | object-name | object-type | object-instance | description | present-value-default | min-present-value | max-present-value | settable | supports COV | hi-limit | low-limit | state-text-reference | unit-code | vendor-specific-address
# prefix: CC, CCe, CC...FC, HVAC, DEA - if specific to a subtype of CC or application | # object instance can be changed in display of CC; 22 is default id
WILO CC BAC | 22 | WILO CC BAC | 8 | 22 |  |  |  |  | N | N
Profile ver. | 22 | Profile ver. | 2 | 0 | version of fieldbus communication profile |  |  |  | N | N |  |  |  | 95
Wink | 22 | Wink | 5 | 16 | write an 1 will blink the fieldbus symbol on GT12 |  |  |  | Y | N
box type | 22 | box type | 19 | 32 | subtype of CC panel |  |  |  | N | N |  |  | 1
PLC version | 22 | PLC version | 2 | 48 | application software version for PLC of CC panel |  |  |  | N | N |  |  |  | 95
HMI version | 22 | HMI version | 2 | 80 | application software version for PLC of CC panel |  |  |  | N | N |  |  |  | 95
Box id | 22 | Box id | 2 | 112 | serial number of this CC panel |  |  |  | N | N |  |  |  | 95
Circuit nr | 22 | Circuit nr | 2 | 144 | number of circuit drawing of this CC panel |  |  |  | N | N |  |  |  | 95
Build month | 22 | Build month | 2 | 176 | month when panel was built |  |  |  | N | N |  |  |  | 95
Build year | 22 | Build year | 2 | 192 | year when panel was built |  |  |  | N | N |  |  |  | 95
Bus c. timer | 22 | Bus c. timer | 19 | 208 | control if HMI is accessible when fieldbus is active |  |  |  | Y | N |  |  | 2
Drives On | 22 | Drives On | 5 | 224 | switch to (de)activate the panel |  |  |  | Y | N
CCe - Hand RPM P1 | 22 | Hand RPM P1 | 2 | 240 | RPM for pump 1 running in manual mode |  |  |  | Y | Y |  |  |  | 98
CCe - Hand RPM P2 | 22 | Hand RPM P2 | 2 | 256 | RPM for pump 2 running in manual mode |  |  |  | Y | Y |  |  |  | 98
CCe - Hand RPM P3 | 22 | Hand RPM P3 | 2 | 272 | RPM for pump 3 running in manual mode |  |  |  | Y | Y |  |  |  | 98
CCe - Hand RPM P4 | 22 | Hand RPM P4 | 2 | 288 | RPM for pump 4 running in manual mode |  |  |  | Y | Y |  |  |  | 98
CCe - Hand RPM P5 | 22 | Hand RPM P5 | 2 | 304 | RPM for pump 5 running in manual mode |  |  |  | Y | Y |  |  |  | 98
CCe - Hand RPM P6 | 22 | Hand RPM P6 | 2 | 320 | RPM for pump 6 running in manual mode |  |  |  | Y | Y |  |  |  | 98
CC...FC - FC on | 22 | FC on | 5 | 368 | For panels with FC controls to (de)activate FC |  |  |  | Y | N
HVAC - Controlmode | 22 | Controlmode | 19 | 384 | current controlmode of HVAC panel |  |  |  | N | N |  |  | 3
Current val. | 22 | Current val. | 2 | 400 | current value from sensor |  |  |  | N | Y |  |  |  | 95
Current SP | 22 | Current SP | 2 | 416 | current setpoint for the automatic |  |  |  | Y | Y |  |  |  | 95
num of pumps | 22 | num of pumps | 2 | 432 | number of pumps installed in the system |  |  |  | N | N |  |  |  | 95
Res. p. act. | 22 | Res. p. act. | 5 | 464 | (De)activate the standby of one pump for error condition of a pump |  |  |  | N | N
Res.p.in use | 22 | Res.p.in use | 5 | 480 | Tells if standby pump is in use due to error of a pump |  |  |  | N | N
Index BLP | 22 | Index BLP | 2 | 496 | one-based index of controlled pump, zero if no BLP active |  |  |  | N | Y |  |  |  | 95
P1 auto | 22 | P1 auto | 5 | 512 | true, if pump 1 is in auto mode |  |  |  | N | N
P1 manu on | 22 | P1 manu on | 5 | 513 | true, if pump 1 is manually switch on |  |  |  | N | N
P1 disabled | 22 | P1 disabled | 5 | 514 | true, if pump 1 is deactivated |  |  |  | N | N
P1 running | 22 | P1 running | 5 | 515 | true, if pump 1 is running |  |  |  | N | N
P1 warning | 22 | P1 warning | 5 | 516 | true, if pump 1 has a warning |  |  |  | N | N
P1 error | 22 | P1 error | 5 | 517 | true, if pump 1 has an error alarm |  |  |  | N | N
P1 res. pump | 22 | P1 res. pump | 5 | 518 | true, if pump 1 is used as standby pump |  |  |  | N | N
P2 auto | 22 | P2 auto | 5 | 528 | true, if pump 2 is in auto mode |  |  |  | N | N
P2 manu on | 22 | P2 manu on | 5 | 529 | true, if pump 2 is manually switch on |  |  |  | N | N
P2 disabled | 22 | P2 disabled | 5 | 530 | true, if pump 2 is deactivated |  |  |  | N | N
P2 running | 22 | P2 running | 5 | 531 | true, if pump 2 is running |  |  |  | N | N
P2 warning | 22 | P2 warning | 5 | 532 | true, if pump 2 has a warning |  |  |  | N | N
P2 error | 22 | P2 error | 5 | 533 | true, if pump 2 has an error alarm |  |  |  | N | N
P2 res. pump | 22 | P2 res. pump | 5 | 534 | true, if pump 2 is used as standby pump |  |  |  | N | N
P3 auto | 22 | P3 auto | 5 | 544 | true, if pump 3 is in auto mode |  |  |  | N | N
P3 manu on | 22 | P3 manu on | 5 | 545 | true, if pump 3 is manually switch on |  |  |  | N | N
P3 disabled | 22 | P3 disabled | 5 | 546 | true, if pump 3 is deactivated |  |  |  | N | N
P3 running | 22 | P3 running | 5 | 547 | true, if pump 3 is running |  |  |  | N | N
P3 warning | 22 | P3 warning | 5 | 548 | true, if pump 3 has a warning |  |  |  | N | N
P3 error | 22 | P3 error | 5 | 549 | true, if pump 3 has an error alarm |  |  |  | N | N
P3 res. pump | 22 | P3 res. pump | 5 | 550 | true, if pump 3 is used as standby pump |  |  |  | N | N
P4 auto | 22 | P4 auto | 5 | 560 | true, if pump 4 is in auto mode |  |  |  | N | N
P4 manu on | 22 | P4 manu on | 5 | 561 | true, if pump 4 is manually switch on |  |  |  | N | N
P4 disabled | 22 | P4 disabled | 5 | 562 | true, if pump 4 is deactivated |  |  |  | N | N
P4 running | 22 | P4 running | 5 | 563 | true, if pump 4 is running |  |  |  | N | N
P4 warning | 22 | P4 warning | 5 | 564 | true, if pump 4 has a warning |  |  |  | N | N
P4 error | 22 | P4 error | 5 | 565 | true, if pump 4 has an error alarm |  |  |  | N | N
P4 res. pump | 22 | P4 res. pump | 5 | 566 | true, if pump 4 is used as standby pump |  |  |  | N | N
P5 auto | 22 | P5 auto | 5 | 576 | true, if pump 5 is in auto mode |  |  |  | N | N
P5 manu on | 22 | P5 manu on | 5 | 577 | true, if pump 5 is manually switch on |  |  |  | N | N
P5 disabled | 22 | P5 disabled | 5 | 578 | true, if pump 5 is deactivated |  |  |  | N | N
P5 running | 22 | P5 running | 5 | 579 | true, if pump 5 is running |  |  |  | N | N
P5 warning | 22 | P5 warning | 5 | 580 | true, if pump 5 has a warning |  |  |  | N | N
P5 error | 22 | P5 error | 5 | 581 | true, if pump 5 has an error alarm |  |  |  | N | N
P5 res. pump | 22 | P5 res. pump | 5 | 582 | true, if pump 5 is used as standby pump |  |  |  | N | N
P6 auto | 22 | P6 auto | 5 | 592 | true, if pump 6 is in auto mode |  |  |  | N | N
P6 manu on | 22 | P6 manu on | 5 | 593 | true, if pump 6 is manually switch on |  |  |  | N | N
P6 disabled | 22 | P6 disabled | 5 | 594 | true, if pump 6 is deactivated |  |  |  | N | N
P6 running | 22 | P6 running | 5 | 595 | true, if pump 6 is running |  |  |  | N | N
P6 warning | 22 | P6 warning | 5 | 596 | true, if pump 6 has a warning |  |  |  | N | N
P6 error | 22 | P6 error | 5 | 597 | true, if pump 6 has an error alarm |  |  |  | N | N
P6 res. pump | 22 | P6 res. pump | 5 | 598 | true, if pump 6 is used as standby pump |  |  |  | N | N
Pump 1 mode | 22 | Pump 1 mode | 19 | 640 | tells or sets the current mode of pump 1 |  |  |  | Y | N |  |  | 4
Pump 2 mode | 22 | Pump 2 mode | 19 | 656 | tells or sets the current mode of pump 2 |  |  |  | Y | N |  |  | 4
Pump 3 mode | 22 | Pump 3 mode | 19 | 672 | tells or sets the current mode of pump 3 |  |  |  | Y | N |  |  | 4
Pump 4 mode | 22 | Pump 4 mode | 19 | 688 | tells or sets the current mode of pump 4 |  |  |  | Y | N |  |  | 4
Pump 5 mode | 22 | Pump 5 mode | 19 | 704 | tells or sets the current mode of pump 5 |  |  |  | Y | N |  |  | 4
Pump 6 mode | 22 | Pump 6 mode | 19 | 720 | tells or sets the current mode of pump 6 |  |  |  | Y | N |  |  | 4
CCe - P ctrl mode | 22 | P ctrl mode | 19 | 768 | for CCe tells the mode of BLP changing if BLP switches on or off |  |  |  | N | N |  |  | 5
CCe - Curr. RPM P1 | 22 | Curr. RPM P1 | 2 | 784 | for CCe the current pump 1 speed in % |  |  |  | N | Y |  |  |  | 98
CCe - Curr. RPM P2 | 22 | Curr. RPM P2 | 2 | 800 | for CCe the current pump 2 speed in % |  |  |  | N | Y |  |  |  | 98
CCe - Curr. RPM P3 | 22 | Curr. RPM P3 | 2 | 816 | for CCe the current pump 3 speed in % |  |  |  | N | Y |  |  |  | 98
CCe - Curr. RPM P4 | 22 | Curr. RPM P4 | 2 | 832 | for CCe the current pump 4 speed in % |  |  |  | N | Y |  |  |  | 98
CCe - Curr. RPM P5 | 22 | Curr. RPM P5 | 2 | 848 | for CCe the current pump 5 speed in % |  |  |  | N | Y |  |  |  | 98
CCe - Curr. RPM P6 | 22 | Curr. RPM P6 | 2 | 864 | for CCe the current pump 6 speed in % |  |  |  | N | Y |  |  |  | 98
HVAC - Temp. feed | 22 | Temp. feed | 2 | 912 | in HVAC systems with temperature option the feeding temperature |  |  |  | N | Y |  |  |  | 62
HVAC - Temp. return | 22 | Temp. return | 2 | 928 | in HVAC systems with temperature option the return temperature |  |  |  | N | Y |  |  |  | 62
HVAC - Temp.ambient | 22 | Temp.ambient | 2 | 944 | in HVAC systems with temperature option the ambient temperature |  |  |  | N | Y |  |  |  | 62
HVAC - Temp.process | 22 | Temp.process | 2 | 960 | in HVAC systems with temperature option the process temperature |  |  |  | N | Y |  |  |  | 62
SBM | 22 | SBM | 5 | 976 | the collective run signal indicates at least on running pump |  |  |  | N | N
SSM | 22 | SSM | 5 | 977 | the collective fault signal indicates an active alarm |  |  |  | N | N
HVAC - Sensor TF ok | 22 | Sensor TF ok | 5 | 992 | in HVAC systems with temperature option the state of feed temp. sensor |  |  |  | N | N
HVAC - Sensor TR ok | 22 | Sensor TR ok | 5 | 993 | in HVAC systems with temperature option the state of return temp. sensor |  |  |  | N | N
HVAC - Sensor TA ok | 22 | Sensor TA ok | 5 | 994 | in HVAC systems with temperature option the state of ambient temp. sensor |  |  |  | N | N
HVAC - Sensor TP ok | 22 | Sensor TP ok | 5 | 995 | in HVAC systems with temperature option the state of process temp. sensor |  |  |  | N | N
HVAC - T. module ok | 22 | T. module ok | 5 | 1056 | in HVAC systems with temperature option the state of temp. module |  |  |  | N | N
Setpoint 1 | 22 | Setpoint 1 | 2 | 1072 | value of first setpoint for the controller |  |  |  | Y | Y |  |  |  | 95
Setpoint 2 | 22 | Setpoint 2 | 2 | 1088 | value of second setpoint for the controller |  |  |  | Y | Y |  |  |  | 95
Setpoint 3 | 22 | Setpoint 3 | 2 | 1104 | value of third setpoint for the controller |  |  |  | Y | Y |  |  |  | 95
Ext.setpoint | 22 | Ext.setpoint | 2 | 1184 | value from analog input for external setpoint |  |  |  | N | Y |  |  |  | 95
Sys. cycles | 22 | Sys. cycles | 2 | 1216 | number of power on for the panel |  |  |  | N | Y |  |  |  | 95
System hours | 22 | System hours | 2 | 1248 | number of hours the panel was powered |  |  |  | N | Y |  |  |  | 71
Cycles P1 | 22 | Cycles P1 | 2 | 1280 | number of on/off cycles for pump 1 |  |  |  | N | Y |  |  |  | 95
Cycles P2 | 22 | Cycles P2 | 2 | 1312 | number of on/off cycles for pump 2 |  |  |  | N | Y |  |  |  | 95
Cycles P3 | 22 | Cycles P3 | 2 | 1344 | number of on/off cycles for pump 3 |  |  |  | N | Y |  |  |  | 95
Cycles P4 | 22 | Cycles P4 | 2 | 1376 | number of on/off cycles for pump 4 |  |  |  | N | Y |  |  |  | 95
Cycles P5 | 22 | Cycles P5 | 2 | 1408 | number of on/off cycles for pump 5 |  |  |  | N | Y |  |  |  | 95
Cycles P6 | 22 | Cycles P6 | 2 | 1440 | number of on/off cycles for pump 6 |  |  |  | N | Y |  |  |  | 95
Tot.Run.h P1 | 22 | Tot.Run.h P1 | 2 | 1536 | total number of hours the pump 1 was running |  |  |  | N | Y |  |  |  | 71
Tot.Run.h P2 | 22 | Tot.Run.h P2 | 2 | 1568 | total number of hours the pump 2 was running |  |  |  | N | Y |  |  |  | 71
Tot.Run.h P3 | 22 | Tot.Run.h P3 | 2 | 1600 | total number of hours the pump 3 was running |  |  |  | N | Y |  |  |  | 71
Tot.Run.h P4 | 22 | Tot.Run.h P4 | 2 | 1632 | total number of hours the pump 4 was running |  |  |  | N | Y |  |  |  | 71
Tot.Run.h P5 | 22 | Tot.Run.h P5 | 2 | 1664 | total number of hours the pump 5 was running |  |  |  | N | Y |  |  |  | 71
Tot.Run.h P6 | 22 | Tot.Run.h P6 | 2 | 1696 | total number of hours the pump 6 was running |  |  |  | N | Y |  |  |  | 71
Day.Run.h P1 | 22 | Day.Run.h P1 | 2 | 1792 | number of hours today the pump 1 was running |  |  |  | N | Y |  |  |  | 71
Day.Run.h P2 | 22 | Day.Run.h P2 | 2 | 1808 | number of hours today the pump 2 was running |  |  |  | N | Y |  |  |  | 71
Day.Run.h P3 | 22 | Day.Run.h P3 | 2 | 1824 | number of hours today the pump 3 was running |  |  |  | N | Y |  |  |  | 71
Day.Run.h P4 | 22 | Day.Run.h P4 | 2 | 1840 | number of hours today the pump 4 was running |  |  |  | N | Y |  |  |  | 71
Day.Run.h P5 | 22 | Day.Run.h P5 | 2 | 1856 | number of hours today the pump 5 was running |  |  |  | N | Y |  |  |  | 71
Day.Run.h P6 | 22 | Day.Run.h P6 | 2 | 1872 | number of hours today the pump 6 was running |  |  |  | N | Y |  |  |  | 71
CC...FC - FC Freq | 22 | FC Freq | 2 | 1952 | for CC...FC, the current frequency of the FC |  |  |  | N | Y |  |  |  | 27
CC...FC - FC Curr | 22 | FC Curr | 2 | 1960 | for CC...FC, the actual current of the FC |  |  |  | N | Y |  |  |  | 3
Sensor error | 22 | Sensor error | 5 | 1965 | indcates an sensor alarm |  |  |  | N | N
over press. | 22 | over press. | 5 | 1966 | indicates overpressure alarm |  |  |  | N | N
under press. | 22 | under press. | 5 | 1967 | indicates underpressure alarm |  |  |  | N | N
CC...FC - FC error | 22 | FC error | 5 | 1968 | indicates an FC error |  |  |  | N | N
prepress.low | 22 | prepress.low | 5 | 1969 | indicates dry running of the suction side |  |  |  | N | N
P1 Alarm | 22 | P1 Alarm | 5 | 1970 | indicates an error of the pump 1 |  |  |  | N | N
P2 Alarm | 22 | P2 Alarm | 5 | 1971 | indicates an error of the pump 2 |  |  |  | N | N
P3 Alarm | 22 | P3 Alarm | 5 | 1972 | indicates an error of the pump 3 |  |  |  | N | N
P4 Alarm | 22 | P4 Alarm | 5 | 1973 | indicates an error of the pump 4 |  |  |  | N | N
P5 Alarm | 22 | P5 Alarm | 5 | 1974 | indicates an error of the pump 5 |  |  |  | N | N
P6 Alarm | 22 | P6 Alarm | 5 | 1975 | indicates an error of the pump 6 |  |  |  | N | N
HVAC - Frost | 22 | Frost | 5 | 1978 | for HVAC systems indicates that Frost protection is active |  |  |  | N | N
Battery low | 22 | Battery low | 5 | 1979 | indicates that the PLC backup batterie needs to be changed |  |  |  | N | N
Acknowledge | 22 | Acknowledge | 5 | 1985 | quit current alarms if alarm reason is solved |  |  |  | Y | N
Index Alarm | 22 | Index Alarm | 2 | 1990 | index for the alarm history one wants to see in the following objects |  |  |  | Y | Y |  |  |  | 95
Alarm code | 22 | Alarm code | 2 | 1995 | number of the alarm at the selected index in the history |  |  |  | N | Y |  |  |  | 95
Alarm year | 22 | Alarm year | 2 | 2000 | year when the alarm at the selected index in the history occured |  |  |  | N | Y |  |  |  | 95
Alarm date | 22 | Alarm date | 2 | 2005 | day and month when the alarm at the selected index in the history occured |  |  |  | N | Y |  |  |  | 95
Alarm time | 22 | Alarm time | 2 | 2010 | hour and minute of the day when the alarm at the selected index in the history occured |  |  |  | N | Y |  |  |  | 95
CC...FC - FC type | 22 | FC type | 19 | 2015 | for CC...FC, type the FC installed in the switch box |  |  |  | N | N |  |  | 6
CC...FC - FC ctrl | 22 | FC ctrl | 5 | 2020 | for CC...FC, indicates that FC control is OK |  |  |  | N | N
CC...FC - FC drive | 22 | FC drive | 5 | 2021 | for CC...FC, indicates that FC drive is OK |  |  |  | N | N
CC...FC - FC IF | 22 | FC IF | 5 | 2022 | for CC...FC, indicates that FC interface is OK |  |  |  | N | N
CC...FC - FC warn | 22 | FC warn | 5 | 2023 | for CC...FC, indicates that the FC has active warning |  |  |  | N | N
CC...FC - FC run | 22 | FC run | 5 | 2024 | for CC...FC, indicates that the FC is currently running |  |  |  | N | N
CC...FC - FC w vlt | 22 | FC w vlt | 5 | 2025 | for CC...FC, indicates that the FC has a voltage warning |  |  |  | N | N
CC...FC - FC w cur | 22 | FC w cur | 5 | 2026 | for CC...FC, indicates that the FC has active warning |  |  |  | N | N
CC...FC - FC w tem | 22 | FC w tem | 5 | 2027 | for CC...FC, indicates that the FC has active warning |  |  |  | N | N

## State-Texts
#State Text Reference
#Reference Number | Text 1 or Inactive-Text | Text 2 or Active-Text | Text 3 | Text 4 | Text 5 | ... | Text n
1 | SC | SC...FC | SCe | CC | CC...FC | CCe
2 | Off | Set | Active | Reset | Manual
3 | p-c | dp-c | dp-v | dT-c | dT-v | n(TF) | n(TR) | n(TP) | n(TA) | T(TF)-c | T(TR)-c | T(TP)-c | T(TA)-c | T(AI)-c
4 | Off | Hand | Auto
5 | Cascade | Vario
6 | FC202 | VLT2800 | VLT6000

## Unit-Texts
#Encoding of BACnet Engineering Units
#Code | Unit Text
3 | AMPERES
27 | HERTZ
62 | DEGREES-CELSIUS
71 | HOURS
95 | NO-UNITS
98 | PERCENT

## Object-Types
#Encoding of BACnet Object Types
#Code | Object Type
2 | Analog Value
5 | Binary Value
8 | Device
15 | Notification Class
19 | Multistate Value