## EDE
# Proposal_Engineering-Data-Exchange - B.I.G.-EU
PROJECT_NAME | WILO IF Module BACnet V2.00 | new object in SW 2.00
VERSION_OF_REFERENCEFILE | 1
TIMESTAMP_OF_LAST_CHANGE | 2013-09-06
AUTHOR_OF_LAST_CHANGE | Henner Henkel
VERSION_OF_LAYOUT | 2.1
#mandatory | mandatory | mandatory | mandatory | mandatory | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional
# keyname | device obj.-instance | object-name | object-type | object-instance | description | present-value-default | min-present-value | max-present-value | settable | supports COV | hi-limit | low-limit | state-text-reference | unit-code | vendor-specific-address
System Effective Capacity | n/a | System Effective Capacity | 0 | 0 | scale to max. val. | n/a |  |  |  | N |  |  | n/a | 98
Speed | n/a | Speed | 0 | 1 | speed of master pump | n/a |  |  |  | N |  |  | n/a | 104
Estimated Flow | n/a | Estimated Flow | 0 | 2 | for clear water | n/a |  |  |  | N |  |  | n/a | 135
(Estimated) Pressure | n/a | (Estimated) Pressure | 0 | 3 | estimated = w/o sensor | n/a |  |  |  | N |  |  | n/a | 55
Power Rating | n/a | Power Rating | 0 | 4 | electrical input power | n/a |  |  |  | N |  |  | n/a | 47
Medium Temperature | n/a | Medium Temperature | 0 | 5 | measured at motor housing | n/a |  |  |  | N |  |  | n/a | 62
Operation Time | n/a | Operation Time | 0 | 6 | run time pump(s) | n/a |  |  |  | N |  |  | n/a | 72
Consumption (System) | n/a | Consumption (System) | 0 | 7 |  | n/a |  |  |  | N |  |  | n/a | 19
Min Speed | n/a | Min Speed | 0 | 8 | @ CONST_SPEED mode | n/a |  |  |  | N |  |  | n/a | 104
Max Speed | n/a | Max Speed | 0 | 9 | @ CONST_SPEED mode | n/a |  |  |  | N |  |  | n/a | 104
Min Pressure dp-v | n/a | Min Pressure dp-v | 0 | 10 | @ VAR_DIFFPRESS mode | n/a |  |  |  | N |  |  | n/a | 55
Max Pressure dp-v | n/a | Max Pressure dp-v | 0 | 11 | @ VAR_DIFFPRESS mode | n/a |  |  |  | N |  |  | n/a | 55
Max Flow | n/a | Max Flow | 0 | 12 | full speed/zero head | n/a |  |  |  | N |  |  | n/a | 135
Min Pressure dp-c | n/a | Min Pressure dp-c | 0 | 13 | @ CONST_DIFFPRESS mode | n/a |  |  |  | N |  |  | n/a | 55
Max Pressure dp-c | n/a | Max Pressure dp-c | 0 | 14 | @ CONST_DIFFPRESS mode | n/a |  |  |  | N |  |  | n/a | 55
Max Power | n/a | Max Power | 0 | 15 | electrical input power | n/a |  |  |  | N |  |  | n/a | 47
Bus Setpoint | n/a | Bus Setpoint | 1 | 0 | scale to max. val. | 100.0 |  |  |  | N |  |  | n/a | 98
TEMP_VARIABLE Tmin | n/a | TEMP_VARIABLE Tmin | 1 | 1 |  | 20.0 |  |  |  | N |  |  | n/a | 62
TEMP_VARIABLE Tmax | n/a | TEMP_VARIABLE Tmax | 1 | 2 |  | 40.0 |  |  |  | N |  |  | n/a | 62
TEMP_VARIABLE Pmin | n/a | TEMP_VARIABLE Pmin | 1 | 3 |  | 0.0 |  |  |  | N |  |  | n/a | 55
TEMP_VARIABLE Pmax | n/a | TEMP_VARIABLE Pmax | 1 | 4 |  | 0.0 |  |  |  | N |  |  | n/a | 55
CONST_CONTROL Kp | n/a | CONST_CONTROL Kp | 1 | 5 | PID gain | 0.5 |  |  |  | N |  |  | n/a | 95
CONST_CONTROL Ti | n/a | CONST_CONTROL Ti | 1 | 6 | PID integration time | 0 |  |  |  | N |  |  | n/a | 73
CONST_CONTROL Td | n/a | CONST_CONTROL Td | 1 | 7 | PID derivate time | 0 |  |  |  | N |  |  | n/a | 73
Bus Command Timer timeout | n/a | Bus Command Timer timeout | 1 | 8 |  | 300 |  |  |  | N |  |  | n/a | 73
Preset Setpoint | n/a | Preset Setpoint | 1 | 100 | bus fail / startup | 100.0 |  |  |  | N |  |  | n/a | 98
System Command Pump on | n/a | System Command Pump on | 3 | 0 |  | n/a |  |  |  | N |  |  | n/a | -
System Command off override | n/a | System Command off override | 3 | 1 | also local ext. off terminals | n/a |  |  |  | N |  |  | n/a | -
System Command max override | n/a | System Command max override | 3 | 2 |  | n/a |  |  |  | N |  |  | n/a | -
System Command min override | n/a | System Command min override | 3 | 3 |  | n/a |  |  |  | N |  |  | n/a | -
Status Lower Regulation Limit | n/a | Status Lower Regulation Limit | 3 | 4 |  | n/a |  |  |  | N |  |  | n/a | -
Status Upper Regulation Limit | n/a | Status Upper Regulation Limit | 3 | 5 |  | n/a |  |  |  | N |  |  | n/a | -
Status Setpoint out of Range | n/a | Status Setpoint out of Range | 3 | 6 |  | n/a |  |  |  | N |  |  | n/a | -
Status Setpoint Diff. > 10 % | n/a | Status Setpoint Diff. > 10 % | 3 | 7 |  | n/a |  |  |  | N |  |  | n/a | -
Status Auto Night Active | n/a | Status Auto Night Active | 3 | 8 |  | n/a |  |  |  | N |  |  | n/a | -
Status Ready for Operation | n/a | Status Ready for Operation | 3 | 9 |  | n/a |  |  |  | N |  |  | n/a | -
Status Pump is operating | n/a | Status Pump is operating | 3 | 10 |  | n/a |  |  |  | N |  |  | n/a | -
Status Service required | n/a | Status Service required | 3 | 11 |  | n/a |  |  |  | N |  |  | n/a | -
Status Warning Present | n/a | Status Warning Present | 3 | 12 |  | n/a |  |  |  | N |  |  | n/a | -
Status Error Present | n/a | Status Error Present | 3 | 13 |  | n/a |  |  |  | N |  |  | n/a | -
Status Final Error Present | n/a | Status Final Error Present | 3 | 14 |  | n/a |  |  |  | N |  |  | n/a | -
Status Local Operation Active | n/a | Status Local Operation Active | 3 | 15 | set by infrared | n/a |  |  |  | N |  |  | n/a | -
Status External Setpoint Active | n/a | Status External Setpoint Active | 3 | 16 | menu 5.4.1.0 / preset | 1 |  |  |  | N |  |  | n/a | -
Bus Command Pump on | n/a | Bus Command Pump on | 4 | 0 |  | ACTIVE |  |  |  | N |  |  | n/a | -
Bus Command off override | n/a | Bus Command off override | 4 | 1 | overrides setpoint with 0 % | INACTIVE |  |  |  | N |  |  | n/a | -
Bus Command max override | n/a | Bus Command max override | 4 | 2 | overrides setpoint with 100% | INACTIVE |  |  |  | N |  |  | n/a | -
Bus Command min override | n/a | Bus Command min override | 4 | 3 | overrides setpoint with min | INACTIVE |  |  |  | N |  |  | n/a | -
Preset Command Pump on | n/a | Preset Command Pump on | 4 | 100 | bus fail / startup | ACTIVE |  |  |  | N |  |  | n/a | -
System Control Mode | n/a | System Control Mode | 13 | 0 |  | n/a |  |  |  | N |  |  | 2 | -
Current Warning/Error Message | n/a | Current Warning/Error Message | 13 | 1 |  | n/a |  |  |  | N |  |  | 1 | -
System Command Timer | n/a | System Command Timer | 13 | 2 |  | n/a |  |  |  | N |  |  | 3 | -
Bus Control Mode | n/a | Bus Control Mode | 14 | 0 |  | 1 |  |  |  | N |  |  | 2 | -
Bus Command Timer | n/a | Bus Command Timer | 14 | 1 | if SET once repeat before timeout AO | 1 |  |  |  | N |  |  | 3 | -
Current W/E Msg. Ackn. | n/a | Current W/E Msg. Ackn. | 14 | 2 | set to ACK to see next Error | 1 |  |  |  | N |  |  | 4 | -
External Source | n/a | External Source | 14 | 3 | overrides Bus Setpoint | 1 |  |  |  | N |  |  | 5 | -
Preset Control Mode | n/a | Preset Control Mode | 14 | 100 | bus fail / startup | 1 |  |  |  | N |  |  | 2 | -
Preset External Source | n/a | Preset External Source | 14 | 101 | bus fail / startup | 1 |  |  |  | N |  |  | 5 | -

## EDE_deutsch informativ
# Proposal_Engineering-Data-Exchange - B.I.G.-EU
PROJECT_NAME | WILO IF Module BACnet V2.00 | neu in SW 2.00
VERSION_OF_REFERENCEFILE | 1
TIMESTAMP_OF_LAST_CHANGE | 2013-09-06
AUTHOR_OF_LAST_CHANGE | Henner Henkel
VERSION_OF_LAYOUT | 2.1
#mandatory | mandatory | mandatory | mandatory | mandatory | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional
# keyname | device obj.-instance | object-name | object-type | object-instance | description | present-value-default | min-present-value | max-present-value | settable | supports COV | hi-limit | low-limit | state-text-reference | unit-code | vendor-specific-address
System Effective Capacity | n/a | System aktive Sollwertvorgabe | 0 | 0 | mit max. Wert skalieren | [7 empty] | n/a | 98
Speed | n/a | Drehzahl | 0 | 1 | speed of master pump | [7 empty] | n/a | 104
Estimated Flow | n/a | Durchfluss (berechnet) | 0 | 2 | füe reines Wasser | [7 empty] | n/a | 135
(Estimated) Pressure | n/a | (berechneter) Druck | 0 | 3 | geschätzt = ohne Sensor | [7 empty] | n/a | 55
Power Rating | n/a | Eingangsleistung | 0 | 4 | elektrische Eingangsleistung | [7 empty] | n/a | 47
Medium Temperature | n/a | Medientemperatur | 0 | 5 | gemessen am Motorgehäuse | [7 empty] | n/a | 62
Operation Time | n/a | Betriebsstunden | 0 | 6 | Laufzeit Pumpe(n) | [7 empty] | n/a | 72
Consumption (System) | n/a | Energieverbrauch (System) | 0 | 7 | [8 empty] | n/a | 19
Min Speed | n/a | Min-Drehzahl (System, CONST_SPEED) | 0 | 8 | bei CONST_SPEED | [7 empty] | n/a | 104
Max Speed | n/a | Max-Drehzahl (System, CONST_SPEED) | 0 | 9 | bei CONST_SPEED | [7 empty] | n/a | 104
Min Pressure dp-v | n/a | Min-Druck dp-v (VAR_DIFFPRESS) | 0 | 10 | bei VAR_DIFFPRESS | [7 empty] | n/a | 55
Max Pressure dp-v | n/a | Max-Druck dp-v (VAR_DIFFPRESS) | 0 | 11 | bei VAR_DIFFPRESS | [7 empty] | n/a | 55
Max Flow | n/a | Max-Durchfluss | 0 | 12 | max. Drehzahl / Förderhöhe=0 | [7 empty] | n/a | 135
Min Pressure dp-c | n/a | Min-Druck dp-c | 0 | 13 | bei CONST_DIFFPRESS | [7 empty] | n/a | 55
Max Pressure dp-c | n/a | Max-Druck dp-c | 0 | 14 | bei CONST_DIFFPRESS | [7 empty] | n/a | 55
Max Power | n/a | Max-Leistung | 0 | 15 | elektrische Eingangsleistung | [7 empty] | n/a | 47
Bus Setpoint | n/a | Sollwertvorgabe | 1 | 0 | mit max. Wert skalieren | [7 empty] | n/a | 98
TEMP_VARIABLE Tmin | n/a | dp-c = f(T) Regelart Tmin | 1 | 1 | [8 empty] | n/a | 62
TEMP_VARIABLE Tmax | n/a | dp-c = f(T) Regelart Tmax | 1 | 2 | [8 empty] | n/a | 62
TEMP_VARIABLE Pmin | n/a | dp-c = f(T) Regelart Pmin | 1 | 3 | [8 empty] | n/a | 55
TEMP_VARIABLE Pmax | n/a | dp-c = f(T) Regelart Pmax | 1 | 4 | [8 empty] | n/a | 55
CONST_CONTROL Kp | n/a | PID Kp | 1 | 5 | PID Verstärkung | [7 empty] | n/a | 95
CONST_CONTROL Ti | n/a | PID Ti | 1 | 6 | PID Nachstellzeit | [7 empty] | n/a | 73
CONST_CONTROL Td | n/a | PID Td | 1 | 7 | PID Vorhaltezeit | [7 empty] | n/a | 73
Bus Command Timer timeout | n/a | Zeitgeber Telegrammüberwachung Ablaufzeit | 1 | 8 | [8 empty] | n/a | 73
Preset Setpoint | n/a | Voreinstellung Sollwertvorgabe | 1 | 100 | bei Busfehler / nach Start | [7 empty] | n/a | 98
System Command Pump on | n/a | Status Schaltbefehl Pumpe ein | 3 | 0 | [8 empty] | n/a | -
System Command off override | n/a | Status Übersteuern Pumpe aus | 3 | 1 | auch bei lokalen ext. Off Klemmen | [7 empty] | n/a | -
System Command max override | n/a | Status Übersteuern Pumpe max | 3 | 2 | [8 empty] | n/a | -
System Command min override | n/a | Status Übersteuern Pumpe max | 3 | 3 | [8 empty] | n/a | -
Status Lower Regulation Limit | n/a | Status untere Reglergrenze | 3 | 4 | [8 empty] | n/a | -
Status Upper Regulation Limit | n/a | Status obere Reglergrenze | 3 | 5 | [8 empty] | n/a | -
Status Setpoint out of Range | n/a | Status Sollwertvorgabe außerhalb des Bereichs | 3 | 6 | [8 empty] | n/a | -
Status Setpoint Diff. > 10 % | n/a | Status Sollwertabweichnung > 10 % | 3 | 7 | [8 empty] | n/a | -
Status Auto Night Active | n/a | Status AutoNacht aktiv | 3 | 8 | [8 empty] | n/a | -
Status Ready for Operation | n/a | Status Bereit | 3 | 9 | [8 empty] | n/a | -
Status Pump is operating | n/a | Status Pumpe läuft | 3 | 10 | [8 empty] | n/a | -
Status Service required | n/a | Status Service erforderlich | 3 | 11 | [8 empty] | n/a | -
Status Warning Present | n/a | Status Warnung | 3 | 12 | [8 empty] | n/a | -
Status Error Present | n/a | Status Fehler | 3 | 13 | [8 empty] | n/a | -
Status Final Error Present | n/a | Status endgültiger Fehler | 3 | 14 | [8 empty] | n/a | -
Status Local Operation Active | n/a | Status lokale Vorrangbedienung | 3 | 15 | über Infrarot | [7 empty] | n/a | -
Status External Setpoint Active | n/a | Status Voreinstellung Sollwertvorgabe | 3 | 16 | menü 5.4.1.0 / "Voreinstellung" | [7 empty] | n/a | -
Bus Command Pump on | n/a | Schaltbefehl Pumpe ein | 4 | 0 | [8 empty] | n/a | -
Bus Command off override | n/a | Übersteuern Pumpe aus | 4 | 1 | übersteuert Sollwert mit 0 % | [7 empty] | n/a | -
Bus Command max override | n/a | Übersteuern Pumpe max | 4 | 2 | übersteuert Sollwert mit 100% | [7 empty] | n/a | -
Bus Command min override | n/a | Übersteuern Pumpe max | 4 | 3 | übersteuert Sollwert mit min | [7 empty] | n/a | -
Preset Command Pump on | n/a | Voreinstellung Schaltbefehl Pumpe Ein | 4 | 100 | bei Busfehler / nach Start | [7 empty] | n/a | -
System Control Mode | n/a | Status Regelart | 13 | 0 | [8 empty] | 2 | -
Current Warning/Error Message | n/a | Aktuelle Warnung / Fehler | 13 | 1 | [8 empty] | 1 | -
System Command Timer | n/a | Status Zeitgeber Telegrammüberwachung | 13 | 2 | [8 empty] | 3 | -
Bus Control Mode | n/a | Regelartvorgabe | 14 | 0 | [8 empty] | 2 | -
Bus Command Timer | n/a | Zeitgeber Telegrammüberwachung | 14 | 1 | nach SET vor Ablaufzeit wiederholen | [7 empty] | 3 | -
Current W/E Msg. Ackn. | n/a | Fehler/Warnung bestätigen | 14 | 2 | auf ACK setzen für nächsten Fehler | [7 empty] | 4 | -
External Source | n/a | Sollwertvorgabe extern | 14 | 3 | übersteuert Sollwert | [7 empty] | 5 | -
Preset Control Mode | n/a | Voreinstellung Regelart | 14 | 100 | bei Busfehler / nach Start | [7 empty] | 2 | -
Preset External Source | n/a | Voreinstellung Sollwertvorgabe extern | 14 | 101 | bei Busfehler / nach Start | [7 empty] | 5 | -

## State-Texts
#State Text Reference
#Reference Number | Text 1 or Inactive-Text | Text 2 or Active-Text | Text 3 | Text 4 | Text 5 | Text 6 | Text 7 | Text 8 | Text 9 | Text 10 | Text 11 | Text 12 | Text 13 | Text 14 | Text 15 | Text 16 | Text 17 | Text 18 | Text 19 | Text 20 | Text 21 | Text 22 | Text 23 | Text 24 | Text 25 | Text 26 | Text 27 | Text 28 | Text 29 | Text 30 | Text 31 | Text 32 | Text 33 | Text 34 | Text 35 | Text 36 | Text 37 | Text 38 | Text 39 | Text 40 | Text 41 | Text 42 | Text 43 | Text 44 | Text 45 | Text 46 | Text 47 | Text 48 | Text 49 | Text 50 | Text 51 | Text 52 | Text 53 | Text 54 | Text 55 | Text 56 | Text 57 | Text 58 | Text 59 | Text 60 | Text 61 | Text 62 | Text 63 | Text 64 | Text 65 | Text 66 | Text 67 | Text 68 | Text 69 | Text 70 | Text 71 | Text 72 | Text 73 | Text 74 | Text 75 | Text 76 | Text 77 | Text 78 | Text 79 | Text 80 | Text 81 | Text 82 | Text 83 | Text 84 | Text 85 | Text 86 | Text 87 | Text 88 | Text 89 | Text 90 | Text 91 | Text 92 | Text 93 | Text 94 | Text 95 | Text 96 | Text 97 | Text 98 | Text 99 | Text 100 | Text 101 | Text 102 | Text 103 | Text 104 | Text 105 | Text 106 | Text 107 | Text 108 | Text 109 | Text 110 | Text 111 | Text 112 | Text 113 | Text 114 | Text 115 | Text 116 | Text 117 | Text 118 | Text 119 | Text 120 | Text 121 | Text 122 | Text 123 | Text 124 | Text 125 | Text 126 | Text 127 | Text 128 | Text 129 | Text 130 | Text 131 | Text 132 | Text 133 | Text 134 | Text 135 | Text 136 | Text 137 | Text 138 | Text 139 | Text 140 | Text 141 | Text 142 | Text 143 | Text 144 | Text 145 | Text 146 | Text 147 | Text 148 | Text 149 | Text 150 | Text 151 | Text 152 | Text 153 | Text 154 | Text 155 | Text 156 | Text 157 | Text 158 | Text 159 | Text 160 | Text 161 | Text 162 | Text 163 | Text 164 | Text 165 | Text 166 | Text 167 | Text 168 | Text 169 | Text 170 | Text 171 | Text 172 | Text 173 | Text 174 | Text 175 | Text 176 | Text 177 | Text 178 | Text 179 | Text 180 | Text 181 | Text 182 | Text 183 | Text 184 | Text 185 | Text 186 | Text 187 | Text 188 | Text 189 | Text 190 | Text 191 | Text 192 | Text 193 | Text 194 | Text 195 | Text 196 | Text 197 | Text 198 | Text 199 | Text 200 | Text 201 | Text 202 | Text 203 | Text 204 | Text 205 | Text 206
1 | no error | E001 | E002 | E003 | E004 | E005 | E006 | E007 | E008 | E009 | E010 | E011 | E012 | E013 | E014 | E015 | E016 | E017 | E018 | E019 | E020 | E021 | E022 | E023 | E024 | E025 | E026 | E027 | E028 | E029 | E030 | E031 | E032 | E033 | E034 | E035 | E036 | E037 | E038 | E039 | E040 | E041 | E042 | E043 | E044 | E045 | E046 | E047 | E048 | E049 | E050 | E051 | E052 | E053 | E054 | E055 | E056 | E057 | E058 | E059 | E060 | E061 | E062 | E063 | E064 | E065 | E066 | E067 | E068 | E069 | E070 | E071 | E072 | E073 | E074 | E075 | E076 | E077 | E078 | E079 | E080 | E081 | E082 | E083 | E084 | E085 | E086 | E087 | E088 | E089 | E090 | E091 | E092 | E093 | E094 | E095 | E096 | E097 | E098 | E099 | E100 | E101 | E102 | E103 | E104 | E105 | E106 | E107 | E108 | E109 | E110 | E111 | E112 | E113 | E114 | E115 | E116 | E117 | E118 | E119 | E120 | E121 | E122 | E123 | E124 | E125 | E126 | E127 | E128 | E129 | E130 | E131 | E132 | E133 | E134 | E135 | E136 | E137 | E138 | E139 | E140 | E141 | E142 | E143 | E144 | E145 | E146 | E147 | E148 | E149 | E150 | E151 | E152 | E153 | E154 | E155 | E156 | E157 | E158 | E159 | E160 | E161 | E162 | E163 | E164 | E165 | E166 | E167 | E168 | E169 | E170 | E171 | E172 | E173 | E174 | E175 | E176 | E177 | E178 | E179 | E180 | E181 | E182 | E183 | E184 | E185 | E186 | E187 | E188 | E189 | E190 | E191 | E192 | E193 | E194 | E195 | E196 | E197 | E198 | E199 | E200 | E201 | E202 | E203 | E204 | E205
2 | CONST_SPEED | CONST_FREQ | Text 3: CONST_POWER; Text 4: CONST_HEAD; Text 5: CONST_PRESSURE; Text 6: CONST_DIFFPRESS; Text 7: VAR_DIFFPRESS; Text 8: CONST_FLOW; Text 9: CONST_TEMP; Text 10: CONST_TEMPDIFF; Text 11: CONST_LEV; Text 12: TEMP_VARIABLE; Text 13: CONST_CONTROL
3 | OFF | SET | Text 3: ACTIVE; Text 4: RESET; Text 5: MANUAL; Text 6: SET_PRESET; Text 7: ACTIVE_PRESET; Text 8: RESET_PRESET; Text 9: MANUAL_PRESET
4 | OFF | ACK | Text 3: ACKed
5 | OFF | 0…10 V | Text 3: 2…10 V; Text 4: 0…20 mA; Text 5: 4…20 mA

## Unit-Texts
#Encoding of BACnet Engineering Units
#Code | Unit Text
166 | METERS-PER-SECOND-PER-SECOND
0 | SQUARE-METERS
116 | SQUARE-CENTIMETERS
1 | SQUARE-FEET
115 | SQUARE-INCHES
105 | CURRENCY1
106 | CURRENCY2
107 | CURRENCY3
108 | CURRENCY4
109 | CURRENCY5
110 | CURRENCY6
111 | CURRENCY7
112 | CURRENCY8
113 | CURRENCY9
114 | CURRENCY10
2 | MILLIAMPERES
3 | AMPERES
4 | OHMS
145 | MILLIOHMS
122 | KILOHMS
123 | MEGOHMS
5 | VOLTS
124 | MILLIVOLTS
6 | KILOVOLTS
7 | MEGAVOLTS
8 | VOLT-AMPERES
9 | KILOVOLT-AMPERES
10 | MEGAVOLT-AMPERES
11 | VOLT-AMPERES-REACTIVE
12 | KILOVOLT-AMPERES-REACTIVE
13 | MEGAVOLT-AMPERES-REACTIVE
14 | DEGREES-PHASE
15 | POWER-FACTOR
167 | AMPERES-PER-METER
168 | AMPERES-PER-SQUARE-METER
169 | AMPERES-SQUARE-METERS
170 | FARADS
171 | HENRYS
172 | OHM-METERS
173 | SIEMENS
174 | SIEMENS-PER-METER
175 | TESLAS
176 | VOLTS-PER-DEGREE-KELVIN
177 | VOLTS-PER-METER
178 | WEBERS
16 | JOULES
17 | KILOJOULES
125 | KILOJOULES-PER-KG
126 | MEGAJOULES
18 | WATT-HOURS
19 | KILOWATT-HOURS
146 | MEGAWATT-HOURS
20 | BTUS
147 | KILO-BTUS
148 | MEGA-BTUS
21 | THERMS
22 | TON-HOURS
23 | JOULES-PER-KG-DRY-AIR
149 | KILOJOULES-PER-KG-DRY-AIR
150 | MEGAJOULES-PER-KG-DRY-AIR
24 | BTUS-PER-LB-DRY-AIR
117 | BTUS-PER-POUND
127 | JOULES-PER-DEGREE-KELVIN
151 | KILOJOULES-PER-DEGREE-KELVIN
152 | MEGAJOULES-PER-DEGREE-KELVIN
128 | JOULES-PER-KILOGRAM-DEGREE-KELVIN
153 | NEWTON
25 | CYCLES-PER-HOUR
26 | CYCLES-PER-MINUTE
27 | HERTZ
129 | KILOHERTZ
130 | MEGAHERTZ
131 | PER-HOUR
28 | GRAMS-OF-WATER-PER-KILOGRAM-DRY-AIR
29 | PERCENT-RELATIVE-HUMIDITY
30 | MILLIMETERS
118 | CENTIMETERS
31 | METERS
32 | INCHES
33 | FEET
34 | WATTS-PER-SQUARE-FOOT
35 | WATTS-PER-SQUARE-METER
36 | LUMENS
37 | LUXES
38 | FOOT-CANDLES
179 | CANDELAS
180 | CANDELAS-PER-SQUARE-METER
39 | KILOGRAMS
40 | POUNDS-MASS
41 | TONS
154 | GRAMS-PER-SECOND
155 | GRAMS-PER-MINUTE
42 | KILOGRAMS-PER-SECOND
43 | KILOGRAMS-PER-MINUTE
44 | KILOGRAMS-PER-HOUR
119 | POUNDS-MASS-PER-SECOND
45 | POUNDS-MASS-PER-MINUTE
46 | POUNDS-MASS-PER-HOUR
156 | TONS-PER-HOUR
132 | MILLIWATTS
47 | WATTS
48 | KILOWATTS
49 | MEGAWATTS
50 | BTUS-PER-HOUR
157 | KILO-BTUS-PER-HOUR
51 | HORSEPOWER
52 | TONS-REFRIGERATION
53 | PASCALS
133 | HECTOPASCALS
54 | KILOPASCALS
134 | MILLIBARS
55 | BARS
56 | POUNDS-FORCE-PER-SQUARE-INCH
57 | CENTIMETERS-OF-WATER
58 | INCHES-OF-WATER
59 | MILLIMETERS-OF-MERCURY
60 | CENTIMETERS-OF-MERCURY
61 | INCHES-OF-MERCURY
62 | DEGREES-CELSIUS
63 | DEGREES-KELVIN
64 | DEGREES-FAHRENHEIT
65 | DEGREE-DAYS-CELSIUS
66 | DEGREE-DAYS-FAHRENHEIT
120 | DELTA-DEGREES-FAHRENHEIT
121 | DELTA-DEGREES-KELVIN
181 | DEGREES-KELVIN-PER-HOUR
182 | DEGREES-KELVIN-PER-MINUTE
67 | YEARS
68 | MONTHS
69 | WEEKS
70 | DAYS
71 | HOURS
72 | MINUTES
73 | SECONDS
158 | HUNDREDTHS-SECONDS
159 | MILLISECONDS
160 | NEWTON-METERS
161 | MILLIMETERS-PER-SECOND
162 | MILLIMETERS-PER-MINUTE
74 | METERS-PER-SECOND
163 | METERS-PER-MINUTE
164 | METERS-PER-HOUR
75 | KILOMETERS-PER-HOUR
76 | FEET-PER-SECOND
77 | FEET-PER-MINUTE
78 | MILES-PER-HOUR
79 | CUBIC-FEET
80 | CUBIC-METERS
81 | IMPERIAL-GALLONS
82 | LITERS
83 | US-GALLONS
142 | CUBIC-FEET-PER-SECOND
84 | CUBIC-FEET-PER-MINUTE
85 | CUBIC-METERS-PER-SECOND
165 | CUBIC-METERS-PER-MINUTE
135 | CUBIC-METERS-PER-HOUR
86 | IMPERIAL-GALLONS-PER-MINUTE
87 | LITERS-PER-SECOND
88 | LITERS-PER-MINUTE
136 | LITERS-PER-HOUR
89 | US-GALLONS-PER-MINUTE
90 | DEGREES-ANGULAR
91 | DEGREES-CELSIUS-PER-HOUR
92 | DEGREES-CELSIUS-PER-MINUTE
93 | DEGREES-FAHRENHEIT-PER-HOUR
94 | DEGREES-FAHRENHEIT-PER-MINUTE
137 | KWATT-HOURS-PER-SQUARE-METER
138 | KWATT-HOURS-PER-SQUARE-FOOT
139 | MEGAJOULES-PER-SQUARE-METER
140 | MEGAJOULES-PER-SQUARE-FOOT
95 | NO-UNITS
96 | PARTS-PER-MILLION
97 | PARTS-PER-BILLION
98 | PERCENT
143 | PERCENT-OBSCURATION-PER-FOOT
144 | PERCENT-OBSCURATION-PER-METER
99 | PERCENT-PER-SECOND
100 | PER-MINUTE
101 | PER-SECOND
102 | PSI-PER-DEGREE-FAHRENHEIT
103 | RADIANS
104 | REVOLUTIONS-PER-MINUTE
141 | WATTS-PER-SQUARE-METER-DEGREE-KELVIN
183 | JOULE-SECONDS
184 | RADIANS-PER-SECOND
185 | SQUARE-METERS-PER-NEWTON
186 | KILOGRAMS-PER-CUBIC-METER
187 | NEWTON-SECONDS
188 | NEWTONS-PER-METER
189 | WATTS-PER-SQUARE-METER
190 | WATTS-PER-METER-PER-DEGREE-KELVIN

## Object-Types
#Encoding of BACnet Object Types
#Code | Object Type
0 | Analog Input
1 | Analog Output
2 | Analog Value
3 | Binary Input
4 | Binary Output
5 | Binary Value
6 | Calendar
7 | Command
8 | Device
9 | Event-Enrollment
10 | File
11 | Group
12 | Loop
13 | Multistate Input
14 | Multistate Output
15 | Notification Class
16 | Program
17 | Schedule
18 | Averaging
19 | Multistate Value
20 | Trend Log
21 | Life Safety Point
22 | Life Safety Zone
23 | Accumulator
24 | Pulse Converter